## All
Max. level is 3mm below bottom of vent tube. Top to bottom of tube is 25mm so max is actually 28mm from top where cap screws into vent. | [9 empty] | Date Code | F8 on Neg., Blank Pos.
BD138AAP0434
Equalise if SG in cell <1.25 when fully charged or SG diff. between cells is 0.03 | [9 empty] | Manufactured | August, 2018
Equalisation charge: 15.5V & measure the specific gravity every hour. Discontinue the equalization charge when the SG no longer rises
Factory specification 1.270 - 1.284
| Batt. 1 | Batt. 2 | Batt. 3 | Batt. 4 | Total
Water (mls) | 3115 | 3895 | 2905 | 3915 | 13830
% | 22.52% | 28.16% | 21.01% | 28.31%
|  | Across all batteries |  |  | Individual battery
Date | Temp C | Min. SG | Max. SG | Max. SG Diff. | Max. SG Diff. | V (Avg) | Charge (SG) | SmartGauge | Comment
2019-06-20 | 27 | 1.265 | 1.273 | 0.008 | 0.003 | 12.55 | 95.62% | N/A | New. Set on mains charge at 14.3V overnight
2019-06-21 | 28 | 1.283 | 1.292 | 0.009 | 0.003 | 13.24 | 105.4% | N/A | Levels all rose to 4-5mm above spec. after 16 hours charging
2019-06-22 | 32 | 1.288 | 1.297 | 0.009 | 0.007 | 14.16 | 107.8% | 100%
2019-07-14 | 30 | 1.256 | 1.273 | 0.017 | 0.01 | 0 | 95.12% | 100% | SG measured after adding water (more like 1.29 before watering)
2019-07-15 | 30 | 1.268 | 1.277 | 0.009 | 0.006 | 0 | 99.25% | 91% | 10:00 and SG much higher than Smartgauge
2019-08-21 | 34 | 1.289 | 1.3 | 0.011 | 0.008 | 0 | 109.9% | 100% | Water added after SG measured
2019-08-28 | 33 | 1.275 | 1.288 | 0.013 | 0.009 | 0 | 102% | 100% | SmartGauge was 97%, reset to 100%
2019-09-18 | 30 | 1.265 | 1.277 | 0.012 | 0.007 | 0 | 98.25% | 100% | Water added at 100% SOC 2 days before SG measured
2019-10-18 | 28.5 | 1.295 | 1.305 | 0.01 | 0.007 | 0 | 111.5% | 100% | Water added after SG measured
2019-10-19 | 24.6 | 1.267 | 1.286 | 0.019 | 0.012 | 13.465 | 99.5% | 100% | Power cut on previous day batt. 99% then 100% on 245W solar. Mainly 13.6V on mains overnight after top up.
2021-09-10 | 25 | 0 | 0 | 0 | 0 | 13.24 |  |  | Stored 693 days on 9th Sept. 21, added 120mls initially & rest on 11th
2021-09-11 | 25 | 1.23 | 1.266 | 0.036 | 0.023 | 0 | 83.75% |  | On boost 14.9V 1.5hrs to mix electroyte partially
2021-09-13 | 25 | 1.258 | 1.283 | 0.025 | 0.015 | 0 | 95.7% |  | On boost 14.9V 4.5hrs to mix electroyte partially
2021-09-14 | 27 | 1.283 | 1.298 | 0.015 | 0.009 | 0 | 106.1% |  | On boost 14.9V 13.3A 1hr then 14.31V 6.5A
2021-09-23 | 25 | 1.287 | 1.3 | 0.013 | 0.008 | 0 | 107.8% |  | Water added after SG measured
2022-04-20 | 20 | 1.286 | 1.298 | 0.012 | 0.008 | 0 | 107.7% | 100% | Water added after SG measured
2022-06-12 | 30 | 1.297 | 1.31 | 0.013 | 0.005 | 13.4 | 112.8% | 100% | Water added after SG measured
2022-06-17 | 31 | 1.281 | 1.293 | 0.012 | 0.003 | 0 | 105.8% | 100% | Water added after SG measured
2022-07-17 | 29.7 | 1.276 | 1.29 | 0.014 | 0.01 | 0 | 102.6% | 94% | Water added after SG measured (Smartguage rising quickly from 92% min. with 17A,13.75V solar, 14.1V at reg.)
2022-08-28 | 30.3 | 1.276 | 1.288 | 0.012 | 0.008 | 0 | 101.9% | 100% | Water added after SG measured (Smartguagejust reached 100%)
2022-10-10 | 28 | 0 | 0 | 0 | 0 | 0 |  |  | Large amount of water added, SG not measured
2022-10-12 | 28 | 1.255 | 1.274 | 0.019 | 0.015 | 0 | 93.12% | 100% | Smartguage says 100%. Mains charger boost off since 10th. Turned on again to get 14.2V
2022-10-14 | 20 | 1.267 | 1.283 | 0.016 | 0.01 | 0 | 100.1% | 100% | Smartguage says 100%. Mains charger turned off & on again to get 14.2V. Boost turned off after 4 hours
2023-05-04 | 23 | 1.29 | 1.301 | 0.011 | 0.008 | 0 | 110% | 98% | Water added after SG measured
2023-05-26 | 23 | 1.266 | 1.278 | 0.012 | 0.011 | 0 | 96.5% | 100% | No water added. ePever regulator still on low setting and set to summer config. after these readings
2023-06-05 | 26.3 | 1.286 | 1.298 | 0.012 | 0.01 | 0 | 108% | 100% | Water added after SG measured. Single 100W panel left and ePever back on winter settings
2024-09-10 | 30.5 | 1.262 | 1.283 | 0.021 | 0.012 | 0 | 97.25% | 94% | Water added after SG measured.
2024-09-17 | 30.5 | 1.255 | 1.276 | 0.021 | 0.014 | 0 | 94.88% | 100% | Water added after SG measured.
2024-09-22 | 28 | 1.26 | 1.283 | 0.023 | 0.018 | 0 | 97.88% | 100%
2024-10-13 | 26 | 0 | 0 | 0 | 0 | 0 | 0% | 100%
2024-10-20 | 22.5 | 1.27 | 1.288 | 0.018 | 0.011 | 0 | 101.6% | 100% | Water added after SG measured. All cells overfilled by 20mls
2025-05-20 | 28 | 1.282 | 1.296 | 0.014 | 0.013 | 13.295 | 105.5% | 100% | Water added after SG measured.
2025-06-26 | 30 | 1.263 | 1.272 | 0.009 | 0.007 | 0 | 94.95% | 89% | Water added after SG measured. This would probably reduce charge to about 90% when mixed in.
2025-07-17 | 28 | 1.259 | 1.27 | 0.011 | 0.007 | 9.975 | 93.75% | 100% | Water added when charging at 88%, approx. 20A. SG taken later at 100% charge. Level too high when charged, probably why SG readings are low
2025-08-28 | 30 | 0 | 0 | 0 | 0 | 0 | 0% | 98% | SG not checked as batteries not at 100% and will be check in a couple of days
2025-09-04 | 29.9 | 1.28 | 1.292 | 0.012 | 0.01 | 0 | 104.1% | 100% | Water added after checking SG (All +20mls above level except batt. 3 where 2 cells sl. lower initially and extra added)
2026-04-11 | 25 | 1.276 | 1.29 | 0.014 | 0.014 | 0 | 102.7% | 100% | Water added after checking SG
2026-05-26 | 30 | 1.287 | 1.298 | 0.011 | 0.011 | 0 | 107.6% | 100% | Water added after checking SG
Note on J23: Author: Epever says: Panel 20.7V 0.2A 34.7C To batt. 13.4V at 0.3A Total 408.47kWh
Note on J24: Author: SG measured on Batt. 1, cell 2 after topping up. Tested at 5 min. intervals with 6-8 squirts to mix. 1.19, 1.22, 1.25 Mains charger was left with switch 3 on (i.e. approx. 13.5V, no boost) The mains charger on boost at approx. 14.2V, 8A (Switches 1 & 3 on) The mains charger on boost at approx. 14.85V (Switches 1 & 2 on) Initially 14A 5 mins. 11.9A 60 mins. 11.6A 90 mins. 12A (14.88V) SG measured.
Note on J25: Author: Initially 14.91V 9.8A 40 mins. 14.91V 9.9A 4.5 hrs 14.87V 12.0A SG measured.
Note on J26: Author: Initially 14.91V 9.8A 40 mins. 14.91V 9.9A 4.5 hrs 14.87V 12.0A SG measured.
Note on I40: Author: Reset to show 95%

## Batt1
N.B. Subtract 0.004 from SG for each 5 degrees below 27 degrees to get corrected value for charge | [11 empty] | 6.37V
Cells numbered from -ve end
|  |  | Cell 1 |  | Cell 2 |  | Cell 3 |  | Battery (mls)
Total water |  | mls | 995 |  | 1065 |  | 1055 |  | 3115
Variation across cells |  | % | 31.94% |  | 34.19% |  | 33.87%
|  | Cell 1 |  | Cell 2 |  | Cell 3 |  | Max. Diff. | Average SG | Charge
Date | Voltage | SG | Water (mls) | SG | Water (mls) | SG | Water (mls) | SG | (Temp. Corrected) | Trojan Data | Status
2019-06-20 | 6.28 | 1.27 | 0 | 1.27 | 10 | 1.27 | 0 | 0 | 1.27 | 96.5% | Trojan data Temp. corrected (New)
2019-06-21 | 6.63 | 1.289 | 0 | 1.287 | 0 | 1.289 | 0 | 0.002 | 1.2883 | 106%
2019-06-22 | 7.08 | 1.294 | 0 | 1.293 | 0 | 1.295 | 0 | 0.002 | 1.294 | 109%
2019-07-14 |  | 1.263 | 30 | 1.265 | 30 | 1.273 | 25 | 0.01 | 1.267 | 96% | Trojan data Temp. corrected
2019-07-15 |  | 1.272 | 0 | 1.272 | 0 | 1.275 | 0 | 0.003 | 1.273 | 100% | Trojan data Temp. corrected
2019-08-21 |  | 1.298 | 35 | 1.298 | 40 | 1.3 | 40 | 0.002 | 1.2987 | 111%
2019-08-28 |  | 1.284 | 0 | 1.283 | 0 | 1.286 | 0 | 0.003 | 1.2843 | 103.5%
2019-09-18 |  | 1.275 | 30 | 1.274 | 30 | 1.277 | 30 | 0.003 | 1.2753 | 100% | Trojan data Temp. corrected
2019-10-18 |  | 1.302 | 40 | 1.302 | 55 | 1.302 | 50 | 0 | 1.302 | 112%
2019-10-19 | 6.75 | 1.283 | 0 | 1.276 | 0 | 1.281 | 0 | 0.007 | 1.28 | 100% | Trojan data Temp. corrected
2021-09-10 | 6.63 |  | 210 |  | 220 |  | 210
2021-09-11 |  | 1.238 | 0 | 1.255 | 0 | 1.25 | 0 | 0.017 | 1.2477 | 85%
2021-09-13 |  | 1.27 | 0 | 1.275 | 0 | 1.27 | 0 | 0.005 | 1.2717 | 97.5%
2021-09-14 |  | 1.292 | 0 | 1.291 | 0 | 1.292 | 0 | 0.001 | 1.2917 | 108%
2021-09-23 |  | 1.291 | 30 | 1.291 | 20 | 1.295 | 20 | 0.004 | 1.2923 | 108%
2022-04-20 |  | 1.29 | 20 | 1.298 | 25 | 1.298 | 25 | 0.008 | 1.2953 | 109.5%
2022-06-12 | 6.73 | 1.3 | 35 | 1.305 | 35 | 1.305 | 45 | 0.005 | 1.3033 | 111.5%
2022-06-17 |  | 1.286 |  | 1.288 |  | 1.289 |  | 0.003 | 1.2877 | 106%
2022-07-17 |  | 1.284 | 50 | 1.283 | 50 | 1.285 | 45 | 0.002 | 1.284 | 103.5%
2022-08-28 |  | 1.277 | 40 | 1.282 | 30 | 1.283 | 30 | 0.006 | 1.2807 | 102%
2022-10-10 |  |  | 80 |  | 110 |  | 110 | 0 | 0
2022-10-12 |  | 1.273 |  | 1.273 |  | 1.271 |  | 0.002 | 1.2723 | 97.5%
2022-10-14 |  | 1.282 |  | 1.283 |  | 1.283 |  | 0.001 | 1.2827 | 103%
2023-05-04 |  | 1.295 | 65 | 1.298 | 65 | 1.298 | 65 | 0.003 | 1.297 | 111%
2023-05-26 |  | 1.27 | 0 | 1.274 | 0 | 1.273 | 0 | 0.004 | 1.2723 | 97.5%
2023-06-05 |  | 1.292 | 30 | 1.295 | 30 | 1.298 | 30 | 0.006 | 1.295 | 109.5%
2024-09-10 |  | 1.283 | 50 | 1.282 | 50 | 1.271 | 50 | 0.012 | 1.2787 | 101%
2024-09-17 |  | 1.272 | 0 | 1.276 | 20 | 1.275 | 20 | 0.004 | 1.2743 | 98.5%
2024-09-22 |  | 1.28 | 0 | 1.282 |  | 1.268 |  | 0.014 | 1.2767 | 100%
2024-10-13 |  |  | 70 |  | 60 |  | 60 | 0 | 0
2024-10-20 |  | 1.284 | 20 | 1.288 | 20 | 1.279 | 30 | 0.009 | 1.2837 | 103.5% | All cells overfilled by 20mls
2025-05-20 | 6.66 | 1.292 | 60 | 1.296 | 60 | 1.283 | 70 | 0.013 | 1.2903 | 106.5%
2025-06-26 |  | 1.268 | 60 | 1.272 | 50 | 1.27 | 50 | 0.004 | 1.27 | 96%
2025-07-17 | 6.65 | 1.27 | 40 | 1.267 | 55 | 1.267 | 50 | 0.003 | 1.268 | 95.5%
2025-08-28 |  |  | 80 |  | 80 |  | 80 | 0 | 0
2025-09-04 |  | 1.283 | 20 | 1.291 | 20 | 1.284 | 20 | 0.008 | 1.286 | 104.5%
2026-04-11 |  | 1.285 | 65 | 1.29 | 80 | 1.276 | 100 | 0.014 | 1.2837 | 104%
2026-05-26 |  | 1.293 | 40 | 1.298 | 40 | 1.287 | 40 | 0.011 | 1.2927 | 108.5%
Note on E16: Author: S.G. 1.247 after adding water i.e. 85% SOC but system had not stabilised.
Note on D23: Author: Level sl. Lower than other cells
Note on F32: Author: Overfilled ~2mm
Note on F34: Author: Slightly overfilled
Note on H36: Author: Probably about 10mls too much

## Batt2
Cells numbered from -ve end
|  |  | Cell 1 |  | Cell 2 |  | Cell 3 |  | Battery (mls)
Total water |  | mls | 1295 |  | 1300 |  | 1300 |  | 3895
Variation across cells |  | % | 33.25% |  | 33.38% |  | 33.38%
|  | Cell 1 |  | Cell 2 |  | Cell 3 |  | Max. Diff. | Average SG | Charge
Date | Voltage | SG | Water (mls) | SG | Water (mls) | SG | Water (mls) | SG | (Temp. Corrected) | Trojan Data | Status
2019-06-20 | 6.27 | 1.267 | 0 | 1.267 | 20 | 1.265 | 0 | 0.002 | 1.2663 | 94.5% | Trojan data Temp. corrected (New)
2019-06-21 | 6.62 | 1.288 | 0 | 1.287 | 0 | 1.287 | 0 | 0.001 | 1.2873 | 105.5%
2019-06-22 | 7.08 | 1.292 | 0 | 1.288 | 0 | 1.293 | 0 | 0.005 | 1.291 | 107.5%
2019-07-14 |  | 1.266 | 25 | 1.256 | 10 | 1.26 | 25 | 0.01 | 1.2607 | 93% | Trojan data Temp. corrected (Batt. 2 is lowest SOC)
2019-07-15 |  | 1.274 | 0 | 1.268 | 0 | 1.273 | 0 | 0.006 | 1.2717 | 98.5% | Trojan data Temp. corrected
2019-08-21 |  | 1.296 | 50 | 1.289 | 50 | 1.297 | 50 | 0.008 | 1.294 | 109%
2019-08-28 |  | 1.279 | 0 | 1.275 | 0 | 1.279 | 0 | 0.004 | 1.2777 | 100.5%
2019-09-18 |  | 1.272 | 35 | 1.265 | 30 | 1.268 | 30 | 0.007 | 1.2683 | 96.5% | Trojan data Temp. corrected
2019-10-18 |  | 1.298 | 40 | 1.295 | 40 | 1.297 | 45 | 0.003 | 1.2967 | 111%
2019-10-19 | 6.73 | 1.281 | 0 | 1.278 | 0 | 1.274 | 0 | 0.007 | 1.2777 | 99.5% | Trojan data Temp. corrected
2021-09-10 | 6.61 |  | 220 |  | 220 |  | 230
2021-09-11 |  | 1.238 | 0 | 1.24 | 0 | 1.23 | 0 | 0.01 | 1.236 | 79%
2021-09-13 |  | 1.26 | 0 | 1.265 | 0 | 1.258 | 0 | 0.007 | 1.261 | 92%
2021-09-14 |  | 1.286 | 0 | 1.286 | 0 | 1.283 | 0 | 0.003 | 1.285 | 104%
2021-09-23 |  | 1.291 | 20 | 1.288 | 20 | 1.29 | 20 | 0.003 | 1.2897 | 107%
2022-04-20 |  | 1.292 | 20 | 1.29 | 20 | 1.288 | 20 | 0.004 | 1.29 | 107%
2022-06-12 | 6.7 | 1.3 | 45 | 1.3 | 40 | 1.298 | 40 | 0.002 | 1.2993 | 111%
2022-06-17 |  | 1.289 |  | 1.287 |  | 1.287 |  | 0.002 | 1.2877 | 106%
2022-07-17 |  | 1.285 | 40 | 1.283 | 40 | 1.28 | 40 | 0.005 | 1.2827 | 103%
2022-08-28 |  | 1.281 | 30 | 1.279 | 30 | 1.282 | 30 | 0.003 | 1.2807 | 102%
2022-10-10 |  |  | 110 |  | 130 |  | 120 | 0 | 0
2022-10-12 |  | 1.274 |  | 1.259 |  | 1.266 |  | 0.015 | 1.2663 | 94.5%
2022-10-14 |  | 1.28 |  | 1.276 |  | 1.28 |  | 0.004 | 1.2787 | 101%
2023-05-04 |  | 1.297 | 70 | 1.294 | 65 | 1.296 | 70 | 0.003 | 1.2957 | 110%
2023-05-26 |  | 1.272 | 0 | 1.268 | 0 | 1.268 | 0 | 0.004 | 1.2693 | 96%
2023-06-05 |  | 1.292 | 30 | 1.29 | 30 | 1.29 | 30 | 0.002 | 1.2907 | 107.5% | All cells slightly overfilled
2024-09-10 |  | 1.266 | 60 | 1.27 | 50 | 1.269 | 50 | 0.004 | 1.2683 | 95%
2024-09-17 |  | 1.262 | 20 | 1.263 | 0 | 1.265 | 10 | 0.003 | 1.2633 | 93%
2024-09-22 |  | 1.266 | 0 | 1.272 | 0 | 1.272 | 0 | 0.006 | 1.27 | 96.5%
2024-10-13 |  |  | 60 |  | 80 |  | 70 | 0 | 0
2024-10-20 |  | 1.274 | 20 | 1.279 | 20 | 1.279 | 20 | 0.005 | 1.2773 | 100% | All cells overfilled by 20mls
2025-05-20 | 6.64 | 1.283 | 50 | 1.285 | 60 | 1.285 | 60 | 0.002 | 1.2843 | 103.5%
2025-06-26 |  | 1.265 | 65 | 1.265 | 50 | 1.265 | 50 | 0 | 1.265 | 93.5%
2025-07-17 | 6.65 | 1.263 | 45 | 1.263 | 55 | 1.265 | 45 | 0.002 | 1.2637 | 93.5%
2025-08-28 |  |  | 90 |  | 90 |  | 90 | 0 | 0
2025-09-04 |  | 1.282 | 20 | 1.285 | 20 | 1.285 | 20 | 0.003 | 1.284 | 103.8%
2026-04-11 |  | 1.28 | 80 | 1.28 | 85 | 1.281 | 90 | 0.001 | 1.2803 | 102%
2026-05-26 |  | 1.288 | 50 | 1.29 | 45 | 1.288 | 45 | 0.002 | 1.2887 | 106%
Note on D34: Author: Slightly overfilled
Note on F34: Author: Slightly overfilled
Note on H34: Author: Slightly overfilled
Note on D36: Author: Probably about 10mls too much

## Batt3
Cells numbered from -ve end
|  |  | Cell 1 |  | Cell 2 |  | Cell 3 |  | Battery (mls)
Total water |  | mls | 945 |  | 980 |  | 980 |  | 2905
Variation across cells |  | % | 32.53% |  | 33.73% |  | 33.73%
|  | Cell 1 |  | Cell 2 |  | Cell 3 |  | Max. Diff. | Average SG | Charge
Date | Voltage | SG | Water (mls) | SG | Water (mls) | SG | Water (mls) | SG | (Temp. Corrected) | Trojan Data | Status
2019-06-20 | 6.26 | 1.27 | 10 | 1.271 | 15 | 1.273 | 10 | 0.003 | 1.2713 | 97% | Trojan data Temp. corrected (New)
2019-06-21 | 6.62 | 1.289 | 0 | 1.289 | 0 | 1.292 | 0 | 0.003 | 1.29 | 107%
2019-06-22 | 7.08 | 1.29 | 0 | 1.293 | 0 | 1.297 | 0 | 0.007 | 1.2933 | 108.5%
2019-07-14 |  | 1.266 | 20 | 1.263 | 25 | 1.273 | 20 | 0.01 | 1.2673 | 96% | Trojan data Temp. corrected
2019-07-15 |  | 1.276 | 0 | 1.276 | 0 | 1.277 | 0 | 0.001 | 1.2763 | 100.5% | Trojan data Temp. corrected
2019-08-21 |  | 1.295 | 50 | 1.299 | 40 | 1.3 | 35 | 0.005 | 1.298 | 111%
2019-08-28 |  | 1.279 | 0 | 1.284 | 0 | 1.288 | 0 | 0.009 | 1.2837 | 103.5%
2019-09-18 |  | 1.27 | 20 | 1.274 | 25 | 1.275 | 25 | 0.005 | 1.273 | 99% | Trojan data Temp. corrected
2019-10-18 |  | 1.298 | 50 | 1.299 | 40 | 1.305 | 50 | 0.007 | 1.3007 | 112%
2019-10-19 | 6.74 | 1.274 | 0 | 1.286 | 0 | 1.283 | 0 | 0.012 | 1.281 | 100% | Trojan data Temp. corrected
2021-09-10 | 6.64 |  | 220 |  | 220 |  | 220
2021-09-11 |  | 1.243 | 0 | 1.266 | 0 | 1.255 | 0 | 0.023 | 1.2547 | 88.5%
2021-09-13 |  | 1.268 | 0 | 1.283 | 0 | 1.278 | 0 | 0.015 | 1.2763 | 99.3%
2021-09-14 |  | 1.289 | 0 | 1.293 | 0 | 1.298 | 0 | 0.009 | 1.2933 | 108.5%
2021-09-23 |  | 1.292 | 20 | 1.3 | 30 | 1.3 | 30 | 0.008 | 1.2973 | 110%
2022-04-20 |  | 1.292 | 20 | 1.297 | 20 | 1.296 | 20 | 0.005 | 1.295 | 109.5%
2022-06-12 | 6.67 | 1.31 | 40 | 1.308 | 35 | 1.31 | 40 | 0.002 | 1.3093 | 117.5%
2022-06-17 |  | 1.291 |  | 1.292 |  | 1.293 |  | 0.002 | 1.292 | 108%
2022-07-17 |  | 1.28 | 30 | 1.285 | 30 | 1.29 | 30 | 0.01 | 1.285 | 104%
2022-08-28 |  | 1.28 | 30 | 1.285 | 30 | 1.288 | 30 | 0.008 | 1.2843 | 103.5%
2022-10-10 |  |  | 135 |  | 150 |  | 145 | 0 | 0
2022-10-12 |  | 1.257 |  | 1.261 |  | 1.263 |  | 0.006 | 1.2603 | 91.5%
2022-10-14 |  | 1.271 |  | 1.279 |  | 1.281 |  | 0.01 | 1.277 | 100%
2023-05-04 |  | 1.293 | 60 | 1.3 | 60 | 1.301 | 60 | 0.008 | 1.298 | 112%
2023-05-26 |  | 1.267 | 0 | 1.273 | 0 | 1.278 | 0 | 0.011 | 1.2727 | 98%
2023-06-05 |  | 1.288 | 40 | 1.296 | 40 | 1.298 | 35 | 0.01 | 1.294 | 109%
2024-09-10 |  | 1.268 | 50 | 1.275 | 50 | 1.28 | 60 | 0.012 | 1.2743 | 98.5%
2024-09-17 |  | 1.266 | 20 | 1.272 | 0 | 1.27 | 20 | 0.006 | 1.2693 | 96%
2024-09-22 |  | 1.269 | 0 | 1.283 | 0 | 1.275 | 0 | 0.014 | 1.2757 | 99.5%
2024-10-13 |  |  | 50 |  | 70 |  | 50 | 0 | 0
2024-10-20 |  | 1.278 | 30 | 1.286 | 20 | 1.285 | 40 | 0.008 | 1.283 | 103% | All cells overfilled by 20mls
2025-05-20 | 6.64 | 1.287 | 50 | 1.295 | 80 | 1.291 | 60 | 0.008 | 1.291 | 107.5%
2025-06-26 |  | 1.267 | 55 | 1.272 | 50 | 1.268 | 50 | 0.005 | 1.269 | 95.8%
2025-07-17 | 6.65 | 1.262 | 45 | 1.267 | 45 | 1.267 | 45 | 0.005 | 1.2653 | 93.5%
2025-08-28 |  |  | 90 |  | 90 |  | 90 | 0 | 0
2025-09-04 |  | 1.282 | 20 | 1.288 | 25 | 1.292 | 30 | 0.01 | 1.2873 | 105%
2026-04-11 |  | 1.282 | 90 | 1.284 | 90 | 1.283 | 90 | 0.002 | 1.283 | 103%
2026-05-26 |  | 1.291 | 35 | 1.297 | 40 | 1.293 | 40 | 0.006 | 1.2937 | 109%
Note on F23: Author: Level sl. Lower than other cells
Note on H23: Author: Level sl. Lower than other cells

## Batt4
Cells numbered from -ve end
|  |  | Cell 1 |  | Cell 2 |  | Cell 3 |  | Battery (mls)
Total water |  | mls | 1275 |  | 1320 |  | 1320 |  | 3915
Variation across cells |  | % | 32.57% |  | 33.72% |  | 33.72%
|  | Cell 1 |  | Cell 2 |  | Cell 3 |  | Max. Diff. | Average SG | Charge
Date | Voltage | SG | Water (mls) | SG | Water (mls) | SG | Water (mls) | SG | (Temp. Corrected) | Trojan Data | Status
2019-06-20 | 6.29 | 1.267 | 10 | 1.265 | 15 | 1.267 | 0 | 0.002 | 1.2663 | 94.5% | Trojan data Temp. corrected (New)
2019-06-21 | 6.61 | 1.284 | 0 | 1.283 | 0 | 1.283 | 0 | 0.001 | 1.2833 | 103% | Batt. 4 is lowest SOC
2019-06-22 | 7.08 | 1.29 | 0 | 1.288 | 0 | 1.29 | 0 | 0.002 | 1.2893 | 106% | Batt. 4 is lowest SOC
2019-07-14 |  | 1.266 | 20 | 1.263 | 20 | 1.27 | 15 | 0.007 | 1.2663 | 95.5% | Trojan data Temp. corrected
2019-07-15 |  | 1.274 | 0 | 1.269 | 0 | 1.271 | 0 | 0.005 | 1.2713 | 98% | Trojan data Temp. corrected
2019-08-21 |  | 1.294 | 40 | 1.292 | 50 | 1.292 | 50 | 0.002 | 1.2927 | 108.5%
2019-08-28 |  | 1.279 | 0 | 1.275 | 0 | 1.279 | 0 | 0.004 | 1.2777 | 100.5%
2019-09-18 |  | 1.271 | 25 | 1.27 | 20 | 1.269 | 20 | 0.002 | 1.27 | 97.5% | Trojan data Temp. corrected
2019-10-18 |  | 1.3 | 50 | 1.297 | 55 | 1.297 | 50 | 0.003 | 1.298 | 111%
2019-10-19 | 6.71 | 1.273 | 0 | 1.273 | 0 | 1.267 | 0 | 0.006 | 1.271 | 98.5% | Trojan data Temp. corrected
2021-09-10 | 6.6 |  | 220 |  | 220 |  | 220
2021-09-11 |  | 1.238 | 0 | 1.253 | 0 | 1.238 | 0 | 0.015 | 1.243 | 82.5%
2021-09-13 |  | 1.262 | 0 | 1.266 | 0 | 1.267 | 0 | 0.005 | 1.265 | 94%
2021-09-14 |  | 1.283 | 0 | 1.288 | 0 | 1.283 | 0 | 0.005 | 1.2847 | 104%
2021-09-23 |  | 1.288 | 20 | 1.288 | 20 | 1.287 | 20 | 0.001 | 1.2877 | 106%
2022-04-20 |  | 1.286 | 20 | 1.288 | 20 | 1.288 | 25 | 0.002 | 1.2873 | 105%
2022-06-12 | 6.7 | 1.298 | 40 | 1.297 | 35 | 1.298 | 35 | 0.001 | 1.2977 | 111%
2022-06-17 |  | 1.284 |  | 1.284 |  | 1.281 |  | 0.003 | 1.283 | 103%
2022-07-17 |  | 1.277 | 30 | 1.276 | 30 | 1.277 | 30 | 0.001 | 1.2767 | 100%
2022-08-28 |  | 1.277 | 30 | 1.276 | 30 | 1.28 | 30 | 0.004 | 1.2777 | 100%
2022-10-10 |  |  | 130 |  | 160 |  | 150 | 0 | 0
2022-10-12 |  | 1.257 |  | 1.257 |  | 1.255 |  | 0.002 | 1.2563 | 89%
2022-10-14 |  | 1.27 |  | 1.273 |  | 1.267 |  | 0.006 | 1.27 | 96.5% | Cell 3 only ~95%
2023-05-04 |  | 1.291 | 60 | 1.29 | 60 | 1.29 | 60 | 0.001 | 1.2903 | 107%
2023-05-26 |  | 1.266 | 0 | 1.266 |  | 1.266 |  | 0 | 1.266 | 94.5% | Overfilled last time
2023-06-05 |  | 1.29 | 30 | 1.289 | 30 | 1.286 | 30 | 0.004 | 1.2883 | 106%
2024-09-10 |  | 1.265 | 50 | 1.272 | 50 | 1.262 | 60 | 0.01 | 1.2663 | 94.5%
2024-09-17 |  | 1.26 | 0 | 1.269 | 0 | 1.255 | 10 | 0.014 | 1.2613 | 92% | 3rd cell only 88%,
2024-09-22 |  | 1.266 | 0 | 1.278 | 0 | 1.26 | 0 | 0.018 | 1.268 | 95.5% | 3rd cell now 92%,
2024-10-13 |  |  | 60 |  | 70 |  | 70 | 0 | 0
2024-10-20 |  | 1.277 | 30 | 1.281 | 20 | 1.27 | 20 | 0.011 | 1.276 | 100% | All cells overfilled by 20mls
2025-05-20 | 6.65 | 1.285 | 60 | 1.29 | 60 | 1.282 | 60 | 0.008 | 1.2857 | 104.5%
2025-06-26 |  | 1.267 | 60 | 1.27 | 60 | 1.263 | 60 | 0.007 | 1.2667 | 94.5%
2025-07-17 |  | 1.26 | 45 | 1.266 | 45 | 1.259 | 45 | 0.007 | 1.2617 | 92.5%
2025-08-28 |  |  | 90 |  | 90 |  | 90 | 0 | 0
2025-09-04 |  | 1.283 | 20 | 1.285 | 20 | 1.28 | 20 | 0.005 | 1.2827 | 103%
2026-04-11 |  | 1.278 | 100 | 1.285 | 100 | 1.277 | 100 | 0.008 | 1.28 | 102%
2026-05-26 |  | 1.292 | 35 | 1.29 | 40 | 1.288 | 50 | 0.004 | 1.29 | 107%
Note on D32: Author: Overfilled ~2mm
Note on F32: Author: Overfilled ~3mm
Note on H32: Author: Overfilled ~2mm